## Sheet1
รายการคำนวณระบบบำบัดน้ำเสีย
ลักษณะของน้ำเสียที่ใช้ในการออกแบบ
Flowrate |  |  | 1000 |  | cum./day
COD |  |  | 5000 |  | mg./l
BOD |  |  | 4000 |  | mg./l.
TKN |  |  | 400 |  | mg./l.
Phosphate |  |  | 18 |  | mg./l.
FOG |  |  | 400 |  | mg./l.
COD Load |  |  | 5000 |  | kg./day
SS |  |  | 700 |  | mg./l.
Equalization Tank 1
Detention Time |  |  | 5 |  | Hr.
Volume Required |  |  | 208.3333 |  | cum.
Width |  |  | 10 |  | m.
Length |  |  | 12 |  | m.
Total Height |  |  | 2.2 |  | m.
Freeboard |  |  | 0.25 |  | m.
Depth of Wastewater |  |  | 1.95 |  | m.
Volume of Tank |  |  | 264 |  | cum.
Volume of Wastewater |  |  | 234 |  | cum.
Actual Detention Time |  |  | 5.616 |  | hr.
Presedimentation Tank
Quantity |  |  | 1 |  | unit
Flowrate |  |  | 62.5 |  | cum.
Surface Overflow Rate |  |  | 0.65 |  | m./Hr.
Total Projected Area (Required) |  |  | 96.1538 |  | sq.m.
Plate Dimension
|  | Width | 1.1 |  | m.
|  | Length | 2.43 |  | m.
Inclined Angle |  |  | 55 |  | Deg
Horizantal Projected Area |  |  | 1.5332 |  | sq.m.
Total No. of Plate (required) |  |  | 62.7157 |  | pcs.
No. of plate (using) |  |  | 62 |  | pcs.
Total Progected Area |  |  | 95.0565 |  | sqm.
Plate Spacing |  |  | 7.4 |  | cm.
Plate Spacing (Hor. Direction) |  |  | 9.0337 |  | cm.
Width of Tank(required ,from calculation) |  |  | 2.8 |  | m.
Lenght of Tank(required ,from calculation) |  |  | 2.8005 |  | m.
Width of Tank(using) |  |  | 2.8 |  | m.
Length of Tank(Using) |  |  | 2.8 |  | m.
Actual Surface Overflow Rate |  |  | 0.6575 |  | m./Hr.
Head of Tank | Inclined |  | 2.4905 |  | m.
| Cone |  | 3.4249 |  | m.
| Liftings |  | 0.4 |  | m.
| Total Head |  | 6.3154 |  | m.
Total Width |  |  | 3.2 |  | m.
Total Length |  |  | 4.4938 |  | m.
Efficiency of Removing |  |  | 20 |  | %
|  |  | Influent |  |  | Effluent
COD | mg./l. |  | 5000 |  |  | 4000
BOD | mg./l. |  | 4000 |  |  | 3200
TKN | mg./l. |  | 400 |  |  | 320
FOG | mg./l. |  | 400 |  |  | 320
Equalization Tank 2
Detention Time |  |  | 3.5 |  | Hr.
Volume Required |  |  | 145.8333 |  | cum.
Diameter |  |  | 8 |  | m.
Height |  |  | 3.3 |  | m.
Freeboard |  |  | 0.2 |  | m.
Water Height |  |  | 3.1 |  | m.
Tank Volume |  |  | 165.8761 |  | cum.
Water Volume |  |  | 155.823 |  | cum.
Actual Detention Time |  |  | 3.7398 |  | hr.
UASB
COD Load |  |  | 4000 |  | kg./day
COD Loading |  |  | 5 |  | kg./day
Required Volume |  |  | 800 |  | cum.
% COD Removed |  |  | 70 |  | %
Removed COD |  |  | 2800 |  | mg./l |  |  | 2800 |  | kg./day
Required TKN |  |  | 28 |  | mg./l |  |  | 28 |  | kg./day
Effluent TKN |  |  | 292 |  | mg./l.
Effluent COD |  |  | 1200 |  | mg./l
ปริมาณ กาชที่เกิด |  |  | 0.5 |  | ลบม./kg.COD Removed |  |  | 1400 |  | cum./day
ปริมาณ กาชมีเทน |  |  | 0.35 |  | ลบม./kg.COD Removed |  |  | 980 |  | cum./day
ปริมาณตะกอนที่เกิด |  |  | 0.05 |  | kg./kg.COD Removed |  |  | 140 |  | kg./day
Sizing
| Width | 10.22 |  | m.
| Length | 12 |  | m.
| Total Height | 7.5 |  | m.
| Freeboard | 0.45 |  | m.
Water Depth |  |  | 7.05 |  | m.
Volume of Tank |  |  | 919.8 |  | sqm.
Volume of Water |  |  | 864.612 |  | sqm.
Upflow Velocity |  |  | 0.33975 |  | m./hr.
งานเจาะรูท่อกระจายน้ำเข้า
Flowrate Recycle |  |  | 41.6667 |  | cum./hr
Flowrate น้ำเสีย |  |  | 41.6667 |  | cum./hr
Flowrate รวม |  |  | 83.3333 |  | cum./hr
ความเร็วตอนออกจากรู |  |  | 2 |  | m./sec
Area รวมของรูทั้งหมด |  |  | 0.011574 |  | sqm.
|  |  | 115.7407 |  | sq.cm.
รูเจาะขนาด |  |  | 1 |  | cm.
Aera ของรู |  |  | 0.7854 |  | sq.cm.
จำนวนรู |  |  | 147.3657 |  | รู
ความยาวท่อกระจายทั้งหมด |  |  | 60 |  | m.
ระยะระหว่างรู |  |  | 0.40715 |  | m.
ท่อเจาะรู Recycle
Flowrate Recycle |  |  | 41.6667 |  | cum./hr
ความเร็วตอนออกจากรู |  |  | 1 |  | m./sec
Area รวมของรูทั้งหมด |  |  | 115.7407 |  | sqm.
Aera ของรู |  |  | 0.7854 |  | sq.cm.
จำนวนรู |  |  | 147.3657 |  | รู
ความยาวท่อกระจายทั้งหมด |  |  | 30 |  | m.
ระยะระหว่างรู |  |  | 0.20358 |  | m.
Denitrification & Aeration Tank
Influent COD |  |  | 1200 |  | mg./l.
TKN in |  |  | 292 |  | mg./l.
TKN out |  |  | 60 |  | mg./l.
NO3(out) |  |  | 0 |  | mg./l.
Produced NO3(by nitri) |  |  | 232 |  | mg./l.
Removed NO3- |  |  | 232 |  | mg./l.
COD Required (by denitri) |  |  | 4.4 |  | kg.COD/kgNO3 |  |  | 1020.8 |  | mg./l
COD out |  |  | 179.2 |  | mg./l.
Recycle Ratio |  |  | 3.8667
Aerobic Tank
COD after Denitrification |  |  | 179.2 |  | mg./l.
TKN in |  |  | 292 |  | mg./l.
µm |  |  | 0.5 |  | day-1
T |  |  | 25 |  | °C
DO |  |  | 2.5 |  | mg./l.
KO2 |  |  | 1.3
pH |  |  | 7.2
µ' m |  |  | 0.53695
Y nitri |  |  | 0.2 |  | kgVSS/kg(BOD)
k' |  |  | 2.6847
kd |  |  | 0.05
Qc (min) |  |  | 2.0536 |  | day
Safty Facter |  |  | 4
Qc |  |  | 10 |  | day
U nitri |  |  | 0.75 |  | day-1
Determine the concentration of N
kn |  |  | 1.3092 |  | mg./l.
N eff(ที่สามารถย่อยได้ต่ำสุด) |  |  | 0.50751 |  | mg./l.
Determine the BOD
Y(bod) |  |  | 0.5 |  | kgVSS/kgBOD
kd(bod) |  |  | 0.06 |  | day-1
U BOD |  |  | 0.32 |  | day-1
S0 (COD in) |  |  | 179.2 |  | mg./l.
S |  |  | 20 |  | mg./l.
X (SS) |  |  | 3000 |  | mg./l.
BOD/TKN |  |  | 0.6137
Fraction of nitrify |  |  | 0.5
X (BOD) |  |  | 1500
X (nitri) |  |  | 1500
T(BOD) |  |  | 0.33167 |  | day-1 |  |  | 7.96 |  | hr.
T(n) |  |  | 0.20622 |  | day-1 |  |  | 4.9493 |  | hr.
Volume (by BOD) |  |  | 331.6667 |  | cum.
Volume (by nitri) |  |  | 206.2222 |  | cum.
Volume use |  |  | 331.6667 |  | cum.
Oxygen Demand |  |  | 1219.44 |  | kg./day |  |  | 50.81 |  | kg./hr.
Use lowspeed Surface Aerator |  |  | 15 |  | kw.
Quantity |  |  | 3 |  | set
Oxygen transfer Rape |  |  | 1.3 |  | kg.O2/kw/hr
Total Oxygen Supply |  |  | 58.5 |  | kg.o2/hr.
Tank Dimension
Width |  |  | 7.95 |  | m.
Length |  |  | 30 |  | m.
Height |  |  | 2.9
Freeboard |  |  | 0.4
Water Height |  |  | 2.5
Tank Volume |  |  | 691.65 |  | cum.
Water Volume |  |  | 596.25 |  | cum. | (>331 cum.)
Combine Nitrification Tank
R(Recycle Ratio) |  |  | 3.8667
X denitri |  |  | 1600 |  | mg./l
Udn |  |  | 0.2 |  | day-1
Tdn |  |  | 0.725 |  | day |  |  | 17.4 |  | hr.
|  |  | 725 |  | cum.
Denitification Tank 1
Width |  |  | 6.95 |  | m.
Length |  |  | 23.7 |  | m.
Height |  |  | 4.15
Freeboard |  |  | 0.25
Water Height |  |  | 3.9
Tank Volume |  |  | 683.5673 |  | cum.
Water Volume |  |  | 642.3885 |  | cum.
Sedimentation Tank
Flowrate |  |  | 41.6667 |  | cum./hr.
SOR |  |  | 0.65 |  | m./hr.
Area Required |  |  | 64.1026 |  | sqm. |  | Max.Flowrate |  | 61.7716 | cum./hr.
Diameter |  |  | 9.0343 |  | m.
Use |  |  | 11 |  | m.
Water Height |  |  | 3 |  | m.
Freeboard |  |  | 0.3 |  | m.
Total Height |  |  | 3.3 |  | m.
Volume of Tank |  |  | 313.6095 |  | cum.
Volume of Water |  |  | 285.0995 |  | cum.
กรณ๊ที่วนน้ำหลังการบำบัดไปผสมกับน้ำเสียใน Equalization Tank 2
Flowrate ที่สามารถวนได้ |  |  | 20.1049 |  | cum./hr.
TKN |  |  | 235.3773 |  | mg./l.